Colonial Pine Hills Sanitary District

7806 Croyle Avenue * Rapid City, SD  57702

Phone (605) 348-3113 * www.cphsd.org

Design and Construction REGULATIONS

for

New Water System Piping and Appurtenances

Adopted, May 18, 2004

GENERAL

Description

This document applies to all underground potable water systems and appurtenances installed within the jurisdictional boundaries of Colonial Pine Hills Sanitary District (CPHSD).  The District does not provide wastewater services and is not responsible for piping or disposal of wastewater within the District boundaries.

The developer, design professional, contractors, and representatives of the same, shall ultimately remain responsible for any and all improvements and repair work completed under their respective design, direction, and supervision.

Design Criteria and Standards Specified Elsewhere

City of Rapid City, South Dakota, Design Criteria Manual for Water Distribution Systems and Sanitary Sewer Collection Systems, January 2000 or current edition, shall apply unless CPHSD standards issued in this document are more restrictive.

Recommended Standards for Water Works, “Ten States Standards”, 2003 or current edition.

South Dakota Plumbing Code and National Standard Plumbing Code Illustrated, 1996 or current edition.

American Water Works Association, Applicable Manuals of Water Supply Practices, current editions.

Uniform Fire Code, 1997 or current edition.

Handbook of PVC Pipe Design, Unibell, 1991 or current edition.

Colonial Pine Hills Sanitary District Ordinances.

CPHSD Water Services Handbook.

Related Specifications for Wastewater Improvements

The CPHSD does not provide wastewater services, but the following specifications shall be followed when wastewater facilities conflict with CPHSD water system piping and appurtenances.

Recommended Design Criteria Manual for Wastewater Collection and Treatment Facilities, South Dakota Department of Water and Natural Resources, 1991 or current edition.

Gravity Sanitary Sewer Design and Construction, ASCE Manuals and Reports on Engineering Practice – No. 60 or current edition.

Recommended Standards for Wastewater Facilities, “Ten States Standards”, 1997 or current edition.

Enforcement and Authority

    - The Manager of CPHSD has the authority to interpret and enforce criteria, standards and construction requirements. Conflicts between specifications, design criteria manuals, codes and standards shall be resolved by the Manager.

    - Administrative Rules of South Dakota, ARSD 74.53.05 and 74.53.04.

    - This document is approved by the CPHSD Board of Trustees. District staff and representatives of the District will provide review and enforcement of the requirements.

Specifications and Details

    - City of Rapid City Standard Specifications for Public Works Construction, 2002 Edition with current updates (or most current edition). These specifications shall apply unless CPHSD standards issued in this document are more restrictive. Changes, additions and/or clarifications are listed in Part 2 of this document.

    - City of Rapid City Standard Plates.

Review and  Plan Submittal

    - Two sets (2) of construction plans and associated documentation for proposed water system piping and improvements shall be submitted to the Manager of CPHSD for review by the District engineer and staff. Plan submittals shall be made directly by the developer to CPHSD and shall not be made from other agencies.  Plan submittals are required on all new platting and when the water service extension is for more than one (1) lot.

    - As-built drawings including plan and profiles shall be prepared by the developer and submitted to CPHSD for review upon completion of the construction. The as-built plan drawings shall also be submitted in Autocad electronic format. The electronic drawings shall include lot layouts, right-of-way, easements, water mains and services and associated appurtenances.

    - Plans will be reviewed and returned within ten (10) working days of submittal. Review comments will be made by the District engineer and staff. Plans shall be resubmitted for review and comment after modification. Comments made on the original submittal shall be returned with the new plan submittal.

    - The submittals shall include complete construction plans, profiles, details, detailed specifications, general notes, reports and other information concerning the work. The submittals shall be prepared by a Registered Professional Engineer in the State of South Dakota. Such documents shall be complete, clear, neat, legible, detailed and in a form acceptable to CPHSD and other local, city, county, state or federal review agencies.

    - The report shall include a water system planning report for the ultimate development to be served.   The report shall cover the proposed full-build out of the proposed development and it shall also review how the surrounding areas will be affected. The reports shall also include:  pipe capacities, existing conditions, hydraulic network, available fire flows at peak day demands, projected water usage, system pressures and other information required.

    - CPHSD will approve the proposed water plans after all requirements of the development have been fulfilled.

    - CPHSD review and approval applies only to water facilities. The project must be reviewed and approved by all appropriate local, county and state governing agencies prior to any construction.

    - The Whispering Pines Volunteer Fire Department will also review all water projects and will make review comments available to CPHSD. This review will add 3 working days to the review process for a total review duration of 13 working days.

    - Plans shall be submitted to the South Dakota Environment and Natural Resources by the Developer for review and approval prior to construction

Construction

    - Construction of the proposed water facilities must be constructed by a Contractor holding a current City of Rapid City Water and Sewer Installer’s License.

    - CPHSD personnel shall be given access to the work at all times to make inspections of the work.  The developer is required to provide construction observation services by a registered professional engineer.

    - The professional engineer must certify the project was constructed in conformance with the plans and specifications upon completion.

    - CPHSD will not accept facilities not in conformance with specified standards.

    - Construction may not proceed until CPHSD approves the final plans.

    - Locations:  Water facilities shall be located within the street, alley or right-of-ways unless topography dictates otherwise. Easements are required where the water facilities will be located outside of the right-of-ways.  The developer is responsible for the acquisition and completion of any needed easements.

    - All water appurtenances such as curb stops, meter pits, valves and fire hydrants shall be accessible by motorized vehicle.

    - The developer is responsible for any and all costs and construction required to provide water service to any existing or proposed development within the District boundaries.

    - The project will be accepted into the CPHSD system upon the following:

Construction is complete and facilities can be placed into service for their intended use.

All testing has been completed and the required results have been achieved.

As-built plans and electronic files are provided to CPHSD.

Facilities are in conformance with plans, specifications and CPHSD standards.

Quality Control

    - Source Quality Control:  Materials shall be clearly marked with size, class, type, test pressure and manufacturer’s name.

    - Regulatory Agencies: Pipe for potable water service shall bear the National Sanitation Foundation Seal. AWWA and ASTM standards shall be followed where applicable.

Product Submittals

    - Shop Drawings and Product Data:

Dimensional data for all pipe, fittings and appurtenances.

Material description and conformance with standards.

Affidavit certifying compliance with applicable standards and specifications.

Other items required to review product conformance with standard specifications.

Deliver at least four (4) copies of the shop drawings to the District Manager for review and approval prior to material order and delivery.

WATER PIPING AND APPURTENANCES

Water Mains

    - Water mains shall be PVC AWWA C-900 or C-905, DR 18, Class 150.

    - All main valves shall be mechanical joint non-rising stem resilient seat gate valves. Butterfly valves are not allowed.  Bolts shall be stainless steel per City specification.

    - Ductile iron fittings shall be mechanical joint.

    - Fittings shall be mechanically restrained at all vertical and horizontal bends, all fittings on lowerings, reducers, tees and valves.   Acceptable joint restraining devices shall be EBBA, Uni-Flange or Romac Field Flange. Concrete thrust blocks are required at all other areas not mechanically restrained., such as connection to existing mains, etc.  Pipe joints for PVC water main shall be push-on bell and spigot. Where water main pipe joints are located closer than the restraining length to a restrained valve or fitting, the bell joint shall be restrained with a bell restraint fitting. The designer shall provide restraining length designs.

    - Bolts for mechanical joints shall be NSS “Cor-Ten Blue” corrosion resistant type.

    - Tapping sleeves shall be stainless steel construction with a 150 psi rating. The branch end shall be flanged and stainless steel bolts and nuts shall be provided. A flange by MJ valve shall be installed on the tapping sleeve.  Contractor is responsible for all taps.

    - Testing and disinfection per standard specifications. The Contractor is responsible for all testing, disinfection and water sampling.

Water Service Lines

    - Minimum service line size is 1".  The developer is responsible for sizing of services, but shall meet all minimum sizing requirements.  Buildings serving four meters shall include 2” services, minimum.

    - Tapping saddles and corporation stops are required. Tapping and all materials are the responsibility of the Contractor. CPHSD will not perform taps or provide any materials for the work. Permits are required.

    - Tapping saddles shall be solid band 304 stainless steel construction with stainless steel nuts and bolts. Tapered Buna-N ASTM D-2000 rubber gasketed (Ford FS303 or equal).

    - One inch (1") through two inch (2") diameter shall be Type “K” copper piping. Water service piping for three (3”) shall be PVC service line pipe and shall comply with ASTM D-2241, 250 psi, SDR 21.  Water service piping for four (4”) and larger shall meet the water main specifications.  Locator wire is required on all non-copper services.

    - Curb stops with boxes shall be placed on each new service line at the property line.

    - Curb boxes shall be placed behind the sidewalk (if applicable) and marked with a steel fence post.

    - All curb boxes shall be adjustable and installed to 1" above finish grade.

    - Curb boxes shall be Minneapolis pattern No. 5622 (1-1/2").

    - Individual units shall be metered when there are four (4) or fewer units in a multi-unit building.

    - Meter pits are required for buildings exceeding four (4) units.  The developer is responsible for construction and maintenance of the meter pit.  Remote meter touch pad units compatible with the District system are required.  Meter pits shall remain the property of the Owner, but the District shall maintain access to the meter pit at all times.  The meters shall be calibrated and verified with the Manufacturer on a regular basis, not to exceed five (5) years.

    - The District shall provide the meter for meters 2” and smaller.  Fees shall be paid by the developer for each meter at the current fee schedule.  The developer shall perform the plumbing work and coordinate the meter and remote read installation.

    - The developer shall furnish, maintain, and install all meters over 2” and shall pay the hook-up fee per the current fee schedule.

    - The fee schedule is as follows:

Size of Water Meter	Deposit Amount		Connection Fee

3/4”					$78.00			$  3,500.00

1”						$135.00			$  4,500.00

1 ½” 					$360.00			$  6,000.00

2”						$450.00			$10,000.00

3”						N/A				$12,000.00

4”						N/A				$15,000.00

5” or Larger				N/A				To be determined by Board at the time of request.

Minimum Design Standards for CPHSD Water Systems

The following minimum guidelines shall be met or exceeded, unless public drinking water standards and regulations are more restrictive.  Refer to Section 1.1, 1.2 and current State of South Dakota drinking water regulations for additional information.

| Parameter | CPHSD Selected Standards |
| --- | --- |
| 1. Distribution System Minimum Working Pressure at Peak Day | 40 psi |
| 2. Normal Distribution System Work Pressure | 50-80 psi |
| 3. Residential Maximum Working Pressure (in home) | 80 psi |
| 4. Minimum Working Pressure at Peak Hour Demand | 20 psi |
| 5. Water Main Size | 8" minimum |
| 6. Distribution System Valving | Valve cluster on all sides of pipe intersections, street intersections with an 800’ maximum spacing. |
| Available Residential Fire Flow at Peak Day | City of RC Criteria or AWWA Manuals of Practice |
| Available Commercial Fire Flow at Peak Day | City of RC Criteria or AWWA and Uniform Fire Code |
| Fire Hydrant Spacing | 450’ max. and all intersections and high points. |
| Pipe Cover | 6’ minimum |
| Pipe looping | Required. |
| Fire Flow | The developer is solely responsible for providing fire flows to any development. |

Revised by Board of Trustees, November 21, 2023